1. GENERAL
   1. RELATED DOCUMENTS
      1. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.
   2. SUMMARY
      1. Section includes:
         1. Mechanical and electrified door hardware for:
            1. Swinging doors.
         2. Electronic access control system components.
      2. Exclusions: Unless specifically listed in hardware sets, hardware is not specified in this section for:
         1. Windows
         2. Cabinets (casework), including locks in cabinets
         3. Signage
         4. Toilet accessories
         5. Overhead doors
      3. Related Sections:
         1. Division 01 Section “Alternates” for alternates affecting this section.
         2. Division 07 Section “Joint Sealants” for sealant requirements applicable to threshold installation specified in this section.
         3. Division 08 Section “Openings” for preparing doors and frames for the products specified in this section.
         4. Division 09 sections for touchup finishing or refinishing of existing openings modified by this section.
         5. Division 26 sections for connections to electrical power system and for low-voltage wiring.
         6. Division 28 sections for coordination with other components of electronic access control system.
   3. REFERENCES
      1. Fire/Life Safety
         1. NFPA - National Fire Protection Association
            1. NFPA 70 – National Electric Code
            2. NFPA 80 - Standard for Fire Doors and Fire Windows
            3. NFPA 101 - Life Safety Code
            4. NFPA 105 - Smoke and Draft Control Door Assemblies
         2. State Fire Safety Code.
      2. UL - Underwriters Laboratories

EDIT – Verify if highlighted required for project

* + - 1. UL 10B - Fire Test of Door Assemblies
      2. UL 10C - Positive Pressure Test of Fire Door Assemblies
      3. UL 1784 - Air Leakage Tests of Door Assemblies
      4. UL 305 - Panic Hardware
    1. Accessibility
       1. ADA - Americans with Disabilities Act .
       2. ANSI A117.1 - Accessible and Usable Buildings and Facilities.
    2. DHI - Door and Hardware Institute
       1. Sequence and Format for the Hardware Schedule
       2. Recommended Locations for Builders Hardware
       3. Key Systems and Nomenclature
    3. ANSI - American National Standards Institute
       1. ANSI/BHMA A156.1 - A156.29, and ANSI A156.31 - Standards for Hardware and Specialties
  1. SUBMITTALS
     1. General:
        1. Submit in accordance with Conditions of Contract and Division 01 requirements.
        2. Highlight, encircle, or otherwise specifically identify on submittals deviations from Contract Documents, issues of incompatibility or other issues which may detrimentally affect the Work.
        3. Prior to forwarding submittal, comply with procedures for verifying existing door and frame compatibility for new hardware, as specified in PART 3, “EXAMINATION” article, herein.
     2. Action Submittals:
        1. Product Data: Product data including manufacturers’ technical product data for each item of door hardware, installation instructions, maintenance of operating parts and finish, and other information necessary to show compliance with requirements.
        2. Riser and Wiring Diagrams: After final approval of hardware schedule, submit details of electrified door hardware, indicating:
           1. Wiring Diagrams: For power, signal, and control wiring and including:

Details of interface of electrified door hardware and building safety and security systems.

Schematic diagram of systems that interface with electrified door hardware.

Point-to-point wiring.

Risers.

* + - 1. Samples for Verification: If requested by Architect, submit production sample or sample installations of each type of exposed hardware unit in finish indicated, and tagged with full description for coordination with schedule.
         1. Samples will be returned to supplier in like-new condition. Units that are acceptable to Architect may, after final check of operations, be incorporated into Work, within limitations of key coordination requirements.
      2. Door Hardware Schedule: Submit schedule with hardware sets in vertical format as illustrated by Sequence of Format for the Hardware Schedule as published by the Door and Hardware Institute. Indicate complete designations of each item required for each door or opening, include:
         1. Door Index; include door number, heading number, and Architects hardware set number.
         2. Opening Lock Function Spreadsheet: List locking device and function for each opening.
         3. Type, style, function, size, and finish of each hardware item.
         4. Name and manufacturer of each item.
         5. Fastenings and other pertinent information.
         6. Location of each hardware set cross-referenced to indications on Drawings.
         7. Explanation of all abbreviations, symbols, and codes contained in schedule.
         8. Mounting locations for hardware.
         9. Door and frame sizes and materials.
         10. Name and phone number for local manufacturer's representative for each product.
         11. Operational Description of openings with any electrified hardware (locks, exits, electromagnetic locks, electric strikes, automatic operators, door position switches, magnetic holders or closer/holder units, and access control components). Operational description should include how door will operate on egress, ingress, and fire and smoke alarm connection.

Submittal Sequence: Submit door hardware schedule concurrent with submissions of Product Data, Samples, and Shop Drawings. Coordinate submission of door hardware schedule with scheduling requirements of other work to facilitate fabrication of other work that is critical in Project construction schedule.

* + - 1. Key Schedule:
         1. After Keying Conference, provide keying schedule listing levels of keying as well as explanation of key system's function, key symbols used and door numbers controlled.
         2. Use ANSI A156.28 “Recommended Practices for Keying Systems” as guideline for nomenclature, definitions, and approach for selecting optimal keying system.
         3. Provide 3 copies of keying schedule for review prepared and detailed in accordance with referenced DHI publication. Include schematic keying diagram and index each key to unique door designations.
         4. Index keying schedule by door number, keyset, hardware heading number, cross keying instructions, and special key stamping instructions.
         5. Provide one complete bitting list of key cuts and one key system schematic illustrating system usage and expansion.

Forward bitting list, key cuts and key system schematic directly to Owner, by means as directed by Owner.

* + - * 1. Prepare key schedule by or under supervision of supplier, detailing Owner’s final keying instructions for locks.
      1. Templates: After final approval of hardware schedule, provide templates for doors, frames and other work specified to be factory prepared for door hardware installation.
    1. Informational Submittals:
       1. Qualification Data: For Supplier, Installer and Architectural Hardware Consultant.
       2. Product Certificates for electrified door hardware, signed by manufacturer:
          1. Certify that door hardware approved for use on types and sizes of labeled fire-rated doors complies with listed fire-rated door assemblies.
       3. Certificates of Compliance:
          1. Certificates of compliance for fire-rated hardware and installation instructions if requested by Architect or Authority Having Jurisdiction.
          2. Installer Training Meeting Certification: Letter of compliance, signed by Contractor, attesting to completion of installer training meeting specified in “QUALITY ASSURANCE” article, herein.
          3. Electrified Hardware Coordination Conference Certification: Letter of compliance, signed by Contractor, attesting to completion of electrified hardware coordination conference, specified in “QUALITY ASSURANCE” article, herein.
       4. Product Test Reports: For compliance with accessibility requirements, based on evaluation of comprehensive tests performed by manufacturer and witnessed by qualified testing agency, for door hardware on doors located in accessible routes.
       5. Warranty: Special warranty specified in this Section.
    2. Closeout Submittals:
       1. Operations and Maintenance Data : Provide in accordance with Division 01 and include:
          1. Complete information on care, maintenance, and adjustment; data on repair and replacement parts, and information on preservation of finishes.
          2. Catalog pages for each product.
          3. Name, address, and phone number of local representative for each manufacturer.
          4. Parts list for each product.
          5. Final approved hardware schedule, edited to reflect conditions as-installed.
          6. Final keying schedule
          7. Copies of floor plans with keying nomenclature
          8. As-installed wiring diagrams for each opening connected to power, both low voltage and 110 volts.
          9. Copy of warranties including appropriate reference numbers for manufacturers to identify project.
  1. QUALITY ASSURANCE
     1. Product Substitutions: Comply with product requirements stated in Division 01 and as specified herein.
        1. Where specific manufacturer’s product is named and accompanied by “No Substitute,” including make or model number or other designation, provide product specified. (Note: Certain products have been selected for their unique characteristics and particular project suitability.)
           1. Where no additional products or manufacturers are listed in product category, requirements for “No Substitute” govern product selection.
        2. Where products indicate “acceptable substitute” or “acceptable manufacturer”, provide product from specified manufacturers, subject to compliance with specified requirements and “Single Source Responsibility” requirements stated herein.
     2. Supplier Qualifications and Responsibilities: Recognized architectural hardware supplier with record of successful in-service performance for supplying door hardware similar in quantity, type, and quality to that indicated for this Project and that provides certified Architectural Hardware Consultant (AHC) available to Owner, Architect, and Contractor, at reasonable times during the Work for consultation.
        1. Warehousing Facilities: In Project's vicinity.
        2. Scheduling Responsibility: Preparation of door hardware and keying schedules.
        3. Engineering Responsibility: Preparation of data for electrified door hardware, including Shop Drawings, based on testing and engineering analysis of manufacturer's standard units in assemblies similar to those indicated for this Project.
        4. Coordination Responsibility: Coordinate installation of electronic security hardware with Architect and electrical engineers and provide installation and technical data to Architect and other related subcontractors.
           1. Upon completion of electronic security hardware installation, inspect and verify that all components are working properly.
     3. Installer Qualifications: Qualified tradesmen, skilled in application of commercial grade hardware with record of successful in-service performance for installing door hardware similar in quantity, type, and quality to that indicated for this Project.
     4. Architectural Hardware Consultant Qualifications: Person who is experienced in providing consulting services for door hardware installations that are comparable in material, design, and extent to that indicated for this Project and meets these requirements:
        1. For door hardware, DHI-certified, Architectural Hardware Consultant (AHC).
        2. Can provide installation and technical data to Architect and other related subcontractors.
        3. Can inspect and verify components are in working order upon completion of installation.
        4. Capable of producing wiring diagrams.
        5. Capable of coordinating installation of electrified hardware with Architect and electrical engineers.
     5. Single Source Responsibility: Obtain each type of door hardware from single manufacturer.
        1. Provide electrified door hardware from same manufacturer as mechanical door hardware, unless otherwise indicated.
        2. Manufacturers that perform electrical modifications and that are listed by testing and inspecting agency acceptable to authorities having jurisdiction are acceptable.
     6. Fire-Rated Door Openings: Provide door hardware for fire-rated openings that complies with NFPA 80 and requirements of authorities having jurisdiction. Provide only items of door hardware that are listed and are identical to products tested by Underwriters Laboratories, Intertek Testing Services, or other testing and inspecting organizations acceptable to authorities having jurisdiction for use on types and sizes of doors indicated, based on testing at positive pressure and according to NFPA 252 or UL 10C and in compliance with requirements of fire-rated door and door frame labels.
     7. Smoke- and Draft-Control Door Assemblies: Where smoke- and draft-control door assemblies are required, provide door hardware that meets requirements of assemblies tested according to UL 1784 and installed in compliance with NFPA 105.
        1. Air Leakage Rate: Maximum air leakage of 0.3 cfm/sq. ft. (3 cu. m per minute/sq. m) at tested pressure differential of 0.3-inch wg (75 Pa) of water.
     8. Electrified Door Hardware: Listed and labeled as defined in NFPA 70, Article 100, by testing agency acceptable to authorities having jurisdiction.
     9. Means of Egress Doors: Latches do not require more than 15 lbf (67 N) to release latch. Locks do not require use of key, tool, or special knowledge for operation.
     10. Accessibility Requirements: For door hardware on doors in an accessible route, comply with governing accessibility regulations cited in “REFERENCES” article, herein.
         1. Provide operating devices that do not require tight grasping, pinching, or twisting of wrist and that operate with force of not more than 5 lbf (22.2 N).
         2. Maximum opening-force requirements:
            1. Interior, Non-Fire-Rated Hinged Doors: 5 lbf (22.2 N) applied perpendicular to door.
            2. Sliding or Folding Doors: 5 lbf (22.2 N) applied parallel to door at latch.
            3. Fire Doors: Minimum opening force allowable by authorities having jurisdiction.
         3. Bevel raised thresholds with slope of not more than 1:2. Provide thresholds not more than 1/2 inch (13 mm) high.
         4. Adjust door closer sweep periods so that, from open position of 70 degrees, door will take at least 3 seconds to move to 3 inches (75 mm) from latch, measured to leading edge of door.
     11. Keying Conference: Conduct conference at Project site to comply with requirements in Division 01.
         1. Attendees: Owner, Contractor, Architect, Installer, Owner's security consultant, and Supplier’s Architectural Hardware Consultant.
         2. Incorporate keying conference decisions into final keying schedule after reviewing door hardware keying system including:
            1. Function of building, flow of traffic, purpose of each area, degree of security required, and plans for future expansion.
            2. Preliminary key system schematic diagram.
            3. Requirements for key control system.
            4. Requirements for access control.
            5. Address for delivery of keys.
     12. Pre-installation Conference: Conduct conference at Project site.
         1. Review and finalize construction schedule and verify availability of materials, Installer's personnel, equipment, and facilities needed to make progress and avoid delays.
         2. Inspect and discuss preparatory work performed by other trades.
         3. Inspect and discuss electrical roughing-in for electrified door hardware.
         4. Review sequence of operation for each type of electrified door hardware.
         5. Review required testing, inspecting, and certifying procedures.
     13. Coordination Conferences:
         1. Installation Coordination Conference: Prior to hardware installation, schedule and hold meeting to review questions or concerns related to proper installation and adjustment of door hardware.
            1. Attendees: Door hardware supplier, door hardware installer, Contractor.
            2. After meeting, provide letter of compliance to Architect, indicating when meeting was held and who was in attendance.
         2. Electrified Hardware Coordination Conference: Prior to ordering electrified hardware, schedule and hold meeting to coordinate door hardware with security, electrical, doors and frames, and other related suppliers.
            1. Attendees: electrified door hardware supplier, doors and frames supplier, electrified door hardware installer, electrical subcontractor, Owner, Owner’s security consultant, Architect and Contractor.
            2. After meeting, provide letter of compliance to Architect, indicating when coordination conference was held and who was in attendance.
  2. DELIVERY, STORAGE, AND HANDLING
     1. Inventory door hardware on receipt and provide secure lock-up for hardware delivered to Project site.
     2. Tag each item or package separately with identification coordinated with final door hardware schedule, and include installation instructions, templates, and necessary fasteners with each item or package.
        1. Deliver each article of hardware in manufacturer’s original packaging.
     3. Project Conditions:
        1. Maintain manufacturer-recommended environmental conditions throughout storage and installation periods.
        2. Provide secure lock-up for door hardware delivered to Project, but not yet installed. Control handling and installation of hardware items so that completion of Work will not be delayed by hardware losses both before and after installation.
     4. Protection and Damage:
        1. Promptly replace products damaged during shipping.
        2. Handle hardware in manner to avoid damage, marring, or scratching. Correct, replace or repair products damaged during Work.
        3. Protect products against malfunction due to paint, solvent, cleanser, or any chemical agent.
     5. Deliver keys to manufacturer of key control system for subsequent delivery to Owner.
     6. Deliver keys and permanent cores to Owner by registered mail or overnight package service.
  3. COORDINATION
     1. Coordinate layout and installation of floor-recessed door hardware with floor construction. Cast anchoring inserts into concrete. Concrete, reinforcement, and formwork requirements are specified in Division 03.
     2. Installation Templates: Distribute for doors, frames, and other work specified to be factory prepared. Check Shop Drawings of other work to confirm that adequate provisions are made for locating and installing door hardware to comply with indicated requirements.
     3. Security: Coordinate installation of door hardware, keying, and access control with Owner's security consultant.
     4. Electrical System Roughing-In: Coordinate layout and installation of electrified door hardware with connections to power supplies and building safety and security systems.
     5. Existing Openings: Where hardware components are scheduled for application to existing construction or where modifications to existing door hardware are required, field verify existing conditions and coordinate installation of door hardware to suit opening conditions and to provide proper door operation.
     6. Direct shipments not permitted, unless approved by Contractor.
  4. WARRANTY
     1. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of door hardware that fail in materials or workmanship within specified warranty period.
        1. Warranty Period: Years from date of Substantial Completion, for durations indicated.
           1. Closers:

Mechanical: 30 years.

* + - * 1. Exit Devices:

Mechanical: 3 years.

Electrified: 1 year.

* + - * 1. Locksets:

Mechanical: 3 years.

* + - * 1. Continuous Hinges: Lifetime warranty.
        2. Key Blanks: Lifetime
      1. Warranty does not cover damage or faulty operation due to improper installation, improper use or abuse.
  1. MAINTENANCE
     1. Maintenance Tools:
        1. Furnish complete set of special tools required for maintenance and adjustment of hardware, including changing of cylinders.

1. PRODUCTS
   1. MANUFACTURERS
      1. Approval of manufacturers other than those listed shall be in accordance with QUALITY ASSURANCE article, herein.
      2. Approval of products from manufacturers indicated as “Acceptable Manufacturer” is contingent upon those products providing all functions and features and meeting all requirements of scheduled manufacturer’s product.

|  |  |  |
| --- | --- | --- |
| Item | Scheduled Manufacturer | Acceptable Manufacturer |
| Hinges | Ives (IVE) | McKinney, Stanley |
| Continuous Hinges | Ives (IVE) | Markar, Stanley |
| Electric Power Transfer | Von Duprin (VON) | ABH, Falcon |
| Flush Bolt | Ives (IVE) | Hiawatha, Trimco |
| Locksets & Deadlocks | Schlage (SCH) | Best, Sargent |
| Aluminum Door Locks – Narrow Style | Adams Rite (ADA) | As pre-approved |
| Exit Devices & Mullions | Von Duprin (VON) | Precision, Sargent |
| Electric Strikes | Von Duprin (VON) | HES, Folger Adam |
| Power Supplies | Schlage Electronics (SCE) or Von Duprin (VON) | Precision, Sargent |
| Cylinders & Keying | Schlage (SCH) | Best, Sargent |
| Door Closers | LCN (LCN) | Norton, Sargent |
| Door Trim | Ives (IVE) | Hiawatha, Trimco |
| Protection Plates | Ives (IVE) | Hiawatha, Trimco |
| Overhead Stops | Glynn-Johnson (GLY) | Rixson, Sargent |
| Stops & Holders | Ives (IVE) | Hiawatha, Trimco |
| Thresholds & Weatherstrip | Zero International (ZER) | Pemko, National Guard |
| Silencers | Ives (IVE) | Hiawatha, Trimco |
| Key Cabinets | Telkee (TEL) | HPC, Lund |

* + 1. Hand of Door: Drawings show direction of slide, swing, or hand of each door leaf. Furnish each item of hardware for proper installation and operation of door movement as shown.
    2. Where specified hardware is not adaptable to finished shape or size of members requiring hardware, furnish suitable types having same operation and quality as type specified, subject to Architect's approval.
  1. MATERIALS
     1. Fasteners
        1. Provide hardware manufactured to conform to published templates, generally prepared for machine screw installation.
        2. Furnish screws for installation with each hardware item. Finish exposed (exposed under any condition) screws to match hardware finish, or, if exposed in surfaces of other work, to match finish of this other work including prepared for paint surfaces to receive painted finish.
        3. Provide concealed fasteners for hardware units exposed when door is closed except when no standard units of type specified are available with concealed fasteners. Do not use thru-bolts for installation where bolt head or nut on opposite face is exposed in other work unless thru-bolts are required to fasten hardware securely. Review door specification and advise Architect if thru-bolts are required.
        4. Install hardware with fasteners provided by hardware manufacturer.
     2. Provide screws, bolts, expansion shields, drop plates and other devices necessary for hardware installation.
        1. Where fasteners are exposed to view: Finish to match adjacent door hardware material.
  2. HINGES
     1. Provide five-knuckle, ball bearing hinges.
        1. Manufacturers and Products:
           1. Scheduled Manufacturer and Product: Ives 5BB series.
           2. Acceptable Manufacturers and Products: McKinney TB/T4B series, Stanley FBB Series.
     2. Requirements:
        1. 1-3/4 inch (44 mm) thick doors, up to and including 36 inches (914 mm) wide:
           1. Interior: Standard weight, steel, 4-1/2 inches (114 mm) high
        2. 1-3/4 inch (44 mm) thick doors over 36 inches (914 mm) wide:
           1. Interior: Heavy weight, steel, 5 inches (127 mm) high
        3. 2 inches or thicker doors:
           1. Interior: Heavy weight, steel, 5 inches (127 mm) high
        4. Provide three hinges per door leaf for doors 90 inches (2286 mm) or less in height, and one additional hinge for each 30 inches (762 mm) of additional door height.
        5. Where new hinges are specified for existing doors or existing frames, provide new hinges of identical size to hinge preparation present in existing door or existing frame.
        6. Hinge Pins: Except as otherwise indicated, provide hinge pins as follows:
           1. Steel Hinges: Steel pins
           2. Non-Ferrous Hinges: Stainless steel pins
           3. Out-Swinging Exterior Doors: Non-removable pins
           4. Out-Swinging Interior Lockable Doors: Non-removable pins
           5. Interior Non-lockable Doors: Non-rising pins
        7. Width of hinges: Adjust hinge width as required for door, frame, and wall conditions to allow proper degree of opening.
  3. CONTINUOUS HINGES
     1. Aluminum Geared
        1. Manufacturers:
           1. Scheduled Manufacturer: Ives.
           2. Acceptable Manufacturers: Markar, Stanley.
        2. Requirements:
           1. Provide aluminum geared continuous hinges conforming to ANSI A156.25, Grade 2.
           2. Provide aluminum geared continuous hinges, where specified in the hardware sets, fabricated from 6063-T6 aluminum, with 0.25-inch (6 mm) diameter Teflon coated stainless steel hinge pin.
           3. Provide split nylon bearings at each hinge knuckle for quiet, smooth, self-lubricating operation.
           4. Provide hinges capable of supporting door weights up to 450 pounds, and successfully tested for 1,500,000 cycles.
           5. On fire-rated doors, provide aluminum geared continuous hinges that are classified for use on rated doors by testing agency acceptable to authority having jurisdiction.
           6. Provide aluminum geared continuous hinges with electrified option scheduled in the hardware sets. Provide with sufficient number and wire gage to accommodate electric function of specified hardware.
           7. Install hinges with fasteners supplied by manufacturer.
           8. Provide hinges with symmetrical hole pattern.
  4. ELECTRIC POWER TRANSFER
     1. Manufacturers:
        + 1. Scheduled Manufacturer: Von Duprin
          2. Acceptable Manufacturers: Falcon, ABH
     2. Provide power transfer with electrified options as scheduled in the hardware sets. Provide with number and gage of wires sufficient to accommodate electric function of specified hardware.
     3. Locate electric power transfer per manufacturer’s template and UL requirements, unless interference with operation of door or other hardware items.
  5. FLUSH BOLTS
     1. Manufacturers:
        1. Scheduled Manufacturer: Ives
        2. Acceptable Manufacturers: Hiawatha, Trimco
     2. Requirements:
        1. Provide automatic, constant latching, and manual flush bolts with forged bronze or stainless steel face plates, extruded brass levers, and with wrought brass guides and strikes. Provide 12 inch (305 mm) steel or brass rods at doors up to 90 inches (2286 mm) in height. For doors over 90 inches (2286 mm) in height increase top rods by 6 inches (152 mm) for each additional 6 inches (152 mm) of door height. Provide dust-proof strikes at each bottom flush bolt.
  6. CYLINDRICAL LOCKS – GRADE 1
     1. Manufacturers and Products:
        1. Scheduled Manufacturer and Product: Schlage ND Series
        2. Acceptable Manufacturers and Products: Sargent 10-Line, Best 9K3 Series.
     2. Requirements:
        1. Provide cylindrical locks conforming to ANSI A156.2 Series 4000, Grade 1. Cylinders: Refer to “KEYING” article, herein.
        2. Provide locks with standard 2-3/4 inches (70 mm) backset, unless noted otherwise, with 1/2 inch latch throw. Provide proper latch throw for UL listing at pairs.
        3. Provide locksets with separate anti-rotation thru-bolts, and no exposed screws.
        4. Provide independently operating levers with two external return spring cassettes mounted under roses to prevent lever sag.
        5. Provide standard ASA strikes unless extended lip strikes are necessary to protect trim.
        6. Provide electrified options as scheduled in the hardware sets.
        7. Lever Trim: Solid cast levers without plastic inserts, and wrought roses on both sides.
           1. Lever Design: Schlage Athens.
           2. Tactile Warning (Knurling): Where required by authority having jurisdiction. Provide on levers on exterior (secure side) of doors serving rooms considered to be hazardous.
  7. AUXILIARY LOCKS
     1. Aluminum Door Deadbolt - Narrow Style:
        1. Manufacturer and Product: Adams Rite MS1850 Series
        2. Requirements:
           1. Provide narrow style aluminum door deadbolts as specified. Cylinders: Refer to “KEYING” article, herein.
           2. Provide deadbolts with backset with full 1-13/32 inches (36 mm) throw deadbolt.
           3. Provide manufacturer’s standard strikes unless extended lip strikes are necessary to protect trim.
  8. EXIT DEVICES
     1. Manufacturers and Products:
        1. Scheduled Manufacturer and Product: Von Duprin 99/33A series
        2. Acceptable Manufacturers and Products: Sargent 80 series, Precision Apex series
     2. Requirements:
        1. Provide exit devices tested to ANSI/BHMA A156.3 Grade 1, and UL listed for Panic Exit or Fire Exit Hardware. Cylinders: Refer to “KEYING” article, herein.
        2. Provide touchpad type exit devices, fabricated of brass, bronze, stainless steel, or aluminum, plated to standard architectural finishes to match balance of door hardware.
        3. Touchpad: Extend minimum of one half of door width. Match exit device finish, stainless steel for US26, US26D, US28, US32, and US32D finishes; and for all other finishes, provide compatible finish to exit device. Provide compression springs in devices, latches, and outside trims or controls; tension springs also acceptable.
        4. Provide exit devices with deadlatching feature for security and for future addition of alarm kits and/or other electrified requirements.
        5. Provide exit devices with manufacturer’s approved strikes.
        6. Provide exit devices cut to door width and height. Locate exit devices at height recommended by exit device manufacturer, allowable by governing building codes, and approved by Architect.
        7. Mount mechanism case flush on face of doors, or provide spacers to fill gaps behind devices. Where glass trim or molding projects off face of door, provide glass bead kits.
        8. Provide hex-key dogging at non-fire-rated exit devices, unless specified less dogging.
        9. Removable Mullions: 2 inches (51 mm) x 3 inches (76 mm) steel tube. Where scheduled as keyed removable mullion that is removed by use of a keyed cylinder, which is self-locking when re-installed.
        10. Where lever handles are specified as outside trim for exit devices, provide heavy-duty lever trims with forged or cast escutcheon plates. Provide vandal-resistant levers that will travel to 90-degree down position when more than 35 pounds of torque are applied, and which can easily be re-set.
            1. Lever Style: Match lever style of locksets.
            2. Tactile Warning (Knurling): Where required by authority having jurisdiction. Provide on levers on exterior (secure side) of doors serving rooms considered to be hazardous.
        11. Provide UL labeled fire exit hardware for fire rated openings.
        12. Provide factory drilled weep holes for exit devices used in full exterior application, highly corrosive areas, and where noted in hardware sets.
        13. Provide electrified options as scheduled.
  9. ELECTRIC STRIKES
     1. Manufacturers and Products:
        1. Scheduled Manufacturer and Product: Von Duprin 6000 series
        2. Acceptable Manufacturers and Products: Folger Adam 300 series, HES 1006 series
     2. Requirements:
        1. Provide electric strikes designed for use with type of locks shown at each opening.
        2. Provide electric strikes UL Listed as burglary-resistant.
        3. Where required, provide electric strikes UL Listed for fire doors and frames.
        4. Provide fail-secure type electric strikes, unless specified otherwise.
        5. Coordinate voltage and provide transformers and rectifiers for each strike as required.
  10. POWER SUPPLIES
      1. Manufacturers and Products:
         1. Scheduled Manufacturer and Product: Schlage Electronics or Von Duprin PS900 series
         2. Acceptable Manufacturers and Products: Precision ELR series, Sargent 3500 series
      2. Requirements:
         1. Provide power supplies, recommended and approved by manufacturer of electrified locking component, for operation of electrified locks, electrified exit devices, magnetic locks, electric strikes, and other components requiring power supply.
         2. Provide appropriate quantity of power supplies necessary for proper operation of electrified locking components as recommended by manufacturer of electrified locking components with consideration for each electrified component using power supply, location of power supply, and approved wiring diagrams. Locate power supplies as directed by Architect.
         3. Provide regulated and filtered 24 VDC power supply , and UL class 2 listed.
         4. Options:
            1. Provide power supply, where specified, with internal capability of charging sealed backup batteries 24 VDC, in addition to operating DC load.
            2. Provide sealed batteries for battery back-up at each power supply where specified.
            3. Provide keyed power supply cabinet.
         5. Provide power supply in an enclosure, complete, and requiring 120VAC to fused input.
         6. Provide power supply with emergency release terminals, where specified, that allow release of all devices upon activation of fire alarm system complete with fire alarm input for initiating “no delay” exiting mode.
  11. CYLINDERS
      1. Manufacturer and Product:
         1. Scheduled Manufacturer and Product: Schlage Everest 29.
         2. Acceptable Manufacturers and Products: Best or Sargent Patented.
      2. Requirements: Provide cylinders/cores complying with the following requirements.
         1. Cylinders/cores compliant with ANSI/BHMA A156.5; latest revision, Section 12, Grade 1; permanent cylinders; cylinder face finished to match lockset, manufacturer’s series as indicated.
      3. Full-sized cylinders in the below-listed configuration(s), distributed throughout the Project as indicated.
         1. Conventional Patented cylinder with open keyway with FSIC cores at exit device locations only.
      4. Patent Protection: Cylinders/cores requiring use of restricted, patented keys, patent-protected until the year, 2029.
      5. Nickel silver bottom pins.
      6. Mark permanent cylinders/cores and keys with applicable blind code per DHI publication “Keying Systems and Nomenclature” for identification. Blind code marks shall not include actual key cuts.
      7. Identification stamping provisions must be approved by the Architect and Owner.
      8. Failure to comply with stamping requirements shall be cause for replacement of cylinders/cores involved at no additional cost to Owner.
         1. Forward cylinders/cores to Owner, separately from keys, by means as directed by Owner.
      9. Replaceable Construction Cores.
         1. Provide temporary construction cores replaceable by permanent cores, furnished in accordance with the following requirements.
      10. 12 construction change (day) keys.
          1. Owner or Owner’s Representative will replace temporary construction cores with permanent cores.
  12. KEYING
      1. Keying System: Factory registered, complying with guidelines in ANSI/BHMA A156.28, incorporating decisions made at keying conference.
      2. Keying Requirements – General

EDIT – 3-level multiplex key sections keying hierarchy for Everest 29 R Keyway Family; 4-level hierarchy for Everest 29 S and T series.

* + - 1. Permanent cylinders/cores keyed by the manufacturer according to the following key system.

EDIT – Select one of the following subparagraphs. If not known, select subparagraph a.

* + 1. Keying system as directed by the Owner.
    2. Key Features: Provide keys with the following features.
       1. Patent Protection: Keys and blanks protected by one or more utility patent(s) until the year, 2029.
    3. Keys
       1. Material: Nickel silver; minimum thickness of .107-inch (2.3mm)
    4. Coordinate with cylinder/core and key identification requirements above.
    5. Stamp keys with Owner’s unique key system facility code as established by the manufacturer; key symbol and embossed or stamped with “DO NOT DUPLICATE” along with the “PATENTED” or patent number to enforce the patent protection.
    6. Failure to comply with stamping requirements shall be cause for replacement of keys involved at no additional cost to Owner.
       1. Quantity: Furnish in the following quantities.

EDIT - Retain subparagraphs below that correspond to type of keying system retained above.

* + - * 1. Change (Day) Keys: 3 per cylinder/core.
        2. Permanent Control Keys: 3.
        3. Master Keys: 6.
        4. Unused balance of key blanks shall be furnished to Owner with the cut keys.

NOTE: construction keys are for temporary construction keying option; presentation keys are for presenting to Owner for ceremonial purposes.

* 1. KEY CONTROL SYSTEM
     1. Key Control System Manufacturers:
        1. Scheduled Manufacturer: Telkee
        2. Acceptable Manufacturers: HPC, Lund
     2. Requirements:
        1. Provide key control system, including envelopes, labels, tags with self-locking key clips, receipt forms, 3-way visible card index, temporary markers, permanent markers, and standard metal cabinet, all as recommended by system manufacturer, with capacity for 150% of number of locks required for Project.
           1. Provide complete cross index system set up by hardware supplier, and place keys on markers and hooks in cabinet as determined by final key schedule.
           2. Provide hinged-panel type cabinet for wall mounting.
  2. DOOR CLOSERS
     1. Manufacturers and Products:
        1. Scheduled Manufacturer and Product: LCN 4010/4110 series
        2. Acceptable Manufacturers and Products: Sargent 281/281P10/281TJ or Norton 9500 series factory assembled (without PRV).
     2. Requirements:
        1. Provide door closers conforming to ANSI/BHMA A156.4 Grade 1 requirements by BHMA certified independent testing laboratory. Stamp units with date of manufacture code.
        2. Provide door closers with fully hydraulic, full rack and pinion action with high strength cast iron cylinder, and full complement bearings at shaft.
        3. Cylinder Body: 1-1/2 inch (38 mm) diameter, with 5/8 inch (16 mm) diameter double heat-treated pinion journal.
        4. Hydraulic Fluid: Fireproof, passing requirements of UL10C, and requiring no seasonal closer adjustment for temperatures ranging from 120 degrees F to -30 degrees F.
        5. Spring Power: Continuously adjustable over full range of closer sizes, and providing reduced opening force as required by accessibility codes and standards.
        6. Hydraulic Regulation: By tamper-proof, non-critical valves with separate adjustment for latch speed, general speed, and backcheck.
        7. Provide closers with a solid forged steel main arms and factory assembled heavy-duty forged forearms for parallel arm closers.
        8. Pressure Relief Valve (PRV) Technology: Not permitted.
        9. Finish for Closer Cylinders, Arms, Adapter Plates, and Metal Covers: Powder coating finish which has been certified to exceed 100 hours salt spray testing as described in ANSI Standard A156.4 and ASTM B117, or has special rust inhibitor (SRI).
        10. Provide special templates, drop plates, mounting brackets, or adapters for arms as required for details, overhead stops, and other door hardware items interfering with closer mounting.
  3. DOOR TRIM
     1. Manufacturers:
        1. Scheduled Manufacturer: Ives.
        2. Acceptable Manufacturers: Hiawatha, Trimco.
     2. Requirements:
        1. Provide push plates 4 inches (102 mm) wide by 16 inches (406 mm) high by 0.050 inch (1 mm) thick and beveled 4 edges. Where width of door stile prevents use of 4 inches (102 mm) wide plate, adjust width to fit.
        2. Provide push bars of solid bar stock, diameter and length as scheduled. Provide push bars of sufficient length to span from center to center of each stile. Where required, mount back to back with pull.
        3. Provide offset pulls of solid bar stock, diameter and length as scheduled. Where required, mount back to back with push bar.
        4. Provide flush pulls as scheduled. Where required, provide back-to-back mounted model.
        5. Provide pulls of solid bar stock, diameter and length as scheduled. Where required, mount back to back with push bar.
        6. Provide pull plates 4 inches (102 mm) wide by 16 inches (406 mm) high by 0.050 inch (1 mm) thick, beveled 4 edges, and prepped for pull. Where width of door stile prevents use of 4 inches (102 mm) wide plate, adjust width to fit.
        7. Provide wire pulls of solid bar stock, diameter and length as scheduled.
        8. Provide decorative pulls as scheduled. Where required, mount back to back with pull.
  4. PROTECTION PLATES
     1. Manufacturers:
        1. Scheduled Manufacturer: Ives.
        2. Acceptable Manufacturers: Hiawatha, Trimco.
     2. Requirements:
        1. Provide kick plates, mop plates, and armor plates minimum of 0.050 inch (1 mm) thick as scheduled. Furnish with sheet metal or wood screws, finished to match plates.
        2. Sizes of plates:
           1. Kick Plates: 10 inches (254 mm) high by 2 inches (51 mm) less width of door on single doors, 1 inch (25 mm) less width of door on pairs
           2. Mop Plates: 4 inches (102 mm) high by 2 inches (51 mm) less width of door on single doors, 1 inch (25 mm) less width of door on pairs
           3. Armor Plates: 36 inches (914 mm) high by 2 inches (51 mm) less width of door on single doors, 1 inch (25 mm) less width of door on pairs
  5. OVERHEAD STOPS AND OVERHEAD STOP/HOLDERS
     1. Manufacturers:
        1. Scheduled Manufacturers: Glynn-Johnson
        2. Acceptable Manufacturers: Rixson, Sargent
     2. Requirements:
        1. Provide heavy duty concealed mounted overhead stop or holder as specified for exterior and interior vestibule single acting doors.
        2. Provide heavy duty concealed mounted overhead stop or holder as specified for double acting doors.
        3. Provide heavy or medium duty and concealed or surface mounted overhead stop or holder for interior doors as specified. Provide medium duty surface mounted overhead stop for interior doors and at any door that swings more than 140 degrees before striking wall, open against equipment, casework, sidelights, and where conditions do not allow wall stop or floor stop presents tripping hazard.
        4. Where overhead holders are specified provide friction type at doors without closer and positive type at doors with closer.
  6. DOOR STOPS AND HOLDERS
     1. Manufacturers:
        1. Scheduled Manufacturer: Ives.
        2. Acceptable Manufacturers: Hiawatha, Trimco.
     2. Provide door stops at each door leaf:
        1. Provide wall stops wherever possible. Provide convex type where mortise type locks are used and concave type where cylindrical type locks are used.
        2. Where a wall stop cannot be used, provide universal floor stops for low or high rise options.
        3. Where wall or floor stop cannot be used, provide medium duty surface mounted overhead stop.
  7. THRESHOLDS, SEALS, DOOR SWEEPS, AUTOMATIC DOOR BOTTOMS, AND GASKETING
     1. Manufacturers:
        1. Scheduled Manufacturer: Zero International.
        2. Acceptable Manufacturers: National Guard, Pemko.
     2. Requirements:
        1. Provide thresholds, weatherstripping (including door sweeps, seals, astragals) and gasketing systems (including smoke, sound, and light) as specified and per architectural details. Match finish of other items.
        2. Size of thresholds:
           1. Saddle Thresholds: 1/2 inch (13 mm) high by jamb width by door width
           2. Bumper Seal Thresholds: 1/2 inch (13 mm) high by 5 inches (127 mm) wide by door width
        3. Provide door sweeps, seals, astragals, and auto door bottoms only of type where resilient or flexible seal strip is easily replaceable and readily available.
  8. SILENCERS
     1. Manufacturers:
        1. Scheduled Manufacturer: Ives.
        2. Acceptable Manufacturers: Hiawatha, Trimco.
     2. Requirements:
        1. Provide "push-in" type silencers for hollow metal or wood frames.
        2. Provide one silencer per 30 inches (762 mm) of height on each single frame, and two for each pair frame.
        3. Omit where gasketing is specified.
  9. FINSHES
     1. Finish: BHMA 626/652 (US26D); except:
        1. Continuous Hinges: BHMA 628 (US28)
        2. Push Plates, Pulls, and Push Bars: BHMA 630 (US32D)
        3. Protection Plates: BHMA 630 (US32D)
        4. Overhead Stops and Holders: BHMA 630 (US32D)
        5. Door Closers: Powder Coat to Match
        6. Exit devices on the exterior or in highly corrosive environments: RAL Tiger-Coating Powder Coat to match 628 finish
        7. Wall Stops: BHMA 630 (US32D)
        8. Latch Protectors: BHMA 630 (US32D)
        9. Weatherstripping: Clear Anodized Aluminum
        10. Thresholds: Mill Finish Aluminum

1. EXECUTION
   1. EXAMINATION
      1. Prior to installation of hardware, examine doors and frames, with Installer present, for compliance with requirements for installation tolerances, labeled fire-rated door assembly construction, wall and floor construction, and other conditions affecting performance.
      2. Proceed with installation only after unsatisfactory conditions have been corrected.
   2. INSTALLATION
      1. Mounting Heights: Mount door hardware units at heights to comply with the following, unless otherwise indicated or required to comply with governing regulations.
         1. Standard Steel Doors and Frames: ANSI/SDI A250.8.
         2. Custom Steel Doors and Frames: HMMA 831.
         3. Wood Doors: DHI WDHS.3, "Recommended Locations for Architectural Hardware for Wood Flush Doors."
      2. Install each hardware item in compliance with manufacturer’s instructions and recommendations, using only fasteners provided by manufacturer.
      3. Do not install surface mounted items until finishes have been completed on substrate. Protect all installed hardware during painting.
      4. Set units level, plumb and true to line and location. Adjust and reinforce attachment substrate as necessary for proper installation and operation.
      5. Drill and countersink units that are not factory prepared for anchorage fasteners. Space fasteners and anchors according to industry standards.
      6. Install operating parts so they move freely and smoothly without binding, sticking, or excessive clearance.
      7. Hinges: Install types and in quantities indicated in door hardware schedule but not fewer than quantity recommended by manufacturer for application indicated or one hinge for every 30 inches (750 mm) of door height, whichever is more stringent, unless other equivalent means of support for door, such as spring hinges or pivots, are provided.
      8. Lock Cylinders: Install construction cores to secure building and areas during construction period.
         1. Replace construction cores with permanent cores as indicated in keying section.
      9. Wiring: Coordinate with Division 26, ELECTRICAL sections for:
         1. Conduit, junction boxes and wire pulls.
         2. Connections to and from power supplies to electrified hardware.
         3. Connections to fire/smoke alarm system and smoke evacuation system.
         4. Connection of wire to door position switches and wire runs to central room or area, as directed by Architect.
         5. Testing and labeling wires with Architect’s opening number.
      10. Key Control System: Tag keys and place them on markers and hooks in key control system cabinet, as determined by final keying schedule.
      11. Door Closers: Mount closers on room side of corridor doors, inside of exterior doors, and stair side of stairway doors from corridors. Closers shall not be visible in corridors, lobbies and other public spaces unless approved by Architect.
      12. Power Supplies: Locate power supplies as indicated or, if not indicated, above accessible ceilings or in equipment room, or alternate location as directed by Architect.
          1. Configuration: Provide one power supply for each door opening with electrified door hardware.
      13. Thresholds: Set thresholds in full bed of sealant complying with requirements specified in Division 07 Section "Joint Sealants."
      14. Stops: Provide floor stops for doors unless wall or other type stops are indicated in door hardware schedule. Do not mount floor stops where they may impede traffic or present tripping hazard.
      15. Perimeter Gasketing: Apply to head and jamb, forming seal between door and frame.
      16. Meeting Stile Gasketing: Fasten to meeting stiles, forming seal when doors are closed.
      17. Door Bottoms: Apply to bottom of door, forming seal with threshold when door is closed.
   3. FIELD QUALITY CONTROL
      1. Architectural Hardware Consultant: Engage qualified independent Architectural Hardware Consultant to perform inspections and to prepare inspection reports.
         1. Architectural Hardware Consultant will inspect door hardware and state in each report whether installed work complies with or deviates from requirements, including whether door hardware is properly installed and adjusted.
   4. ADJUSTING
      1. Initial Adjustment: Adjust and check each operating item of door hardware and each door to ensure proper operation or function of every unit. Replace units that cannot be adjusted to operate as intended. Adjust door control devices to compensate for final operation of heating and ventilating equipment and to comply with referenced accessibility requirements.
         1. Electric Strikes: Adjust horizontal and vertical alignment of keeper to properly engage lock bolt.
         2. Door Closers: Adjust sweep period to comply with accessibility requirements and requirements of authorities having jurisdiction.
      2. Occupancy Adjustment: Approximately six months after date of Substantial Completion, Installer's Architectural Hardware Consultant shall examine and readjust each item of door hardware, including adjusting operating forces, as necessary to ensure function of doors, door hardware, and electrified door hardware.
   5. CLEANING AND PROTECTION
      1. Clean adjacent surfaces soiled by door hardware installation.
      2. Clean operating items as necessary to restore proper function and finish.
      3. Provide final protection and maintain conditions that ensure door hardware is without damage or deterioration at time of Substantial Completion.
   6. DEMONSTRATION
      1. Provide training for Owner's maintenance personnel to adjust, operate, and maintain door hardware and door hardware finishes. Refer to Division 01 Section "Demonstration and Training."
   7. DOOR HARDWARE SCHEDULE
      1. Locksets, exit devices, and other hardware items are referenced in the following hardware sets for series, type and function. Refer to the above-specifications for special features, options, cylinders/keying, and other requirements.
      2. Hardware Groups:

Hardware Group No. 01

Provide each PR door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 2 | EA | CONT. HINGE | 112HD EPT | 628 | IVE |
| 2 | EA | POWER TRANSFER | EPT10 | 689 | VON |
| 1 | EA | ELEC PANIC HARDWARE | QEL+-9949-EO | 626 | VON |
| 1 | EA | ELEC PANIC HARDWARE | QEL+-9949-NL-OP-110MD | 626 | VON |
| 1 | EA | RIM CYLINDER | 20-057 | 626 | SCH |
| 2 | EA | 90 DEG OFFSET PULL | 8190HD 10" O | 630 | IVE |
| 2 | EA | OH STOP | 100S | 630 | GLY |
| 2 | EA | SURFACE CLOSER | 4111 EDA | 689 | LCN |
| 2 | EA | MOUNTING PLATE | 4110-18 | 689 | LCN |
| 2 | EA | BLADE STOP SPACER | 4110-61 | 689 | LCN |
| 2 | EA | MEETING STILE SEAL | 8193AA | AL | ZER |
| 2 | EA | DOOR SWEEP | 39A | AL | ZER |
| 1 | EA | THRESHOLD | 625A MSLA-10 | AL | ZER |
| 1 | EA | POWER SUPPLY | PS902 900-2RS | LGR | VON |

Perimeter weatherstripping by aluminum door manufacturer.  
  
Credential reader device and interfacing with the "QEL" electric latch retraction feature inside the exit device is by the security system supplier.  
  
Power for the "QEL" electric latch retraction feature is by the PS902 power supply.

Hardware Group No. 02

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 1 | EA | PANIC HARDWARE | 99-NL-OP-110MD | 626 | VON |
| 1 | EA | RIM CYLINDER | 20-057 | 626 | SCH |
| 1 | EA | ELECTRIC STRIKE | 6300 FSE | 630 | VON |
| 1 | EA | 90 DEG OFFSET PULL | 8190HD 10" O | 630 | IVE |
| 1 | EA | OH STOP | 100S | 630 | GLY |
| 1 | EA | SURFACE CLOSER | 4111 EDA | 689 | LCN |
| 1 | EA | MOUNTING PLATE | 4110-18 | 689 | LCN |
| 1 | EA | BLADE STOP SPACER | 4110-61 | 689 | LCN |
| 1 | EA | DOOR SWEEP | 39A | AL | ZER |
| 1 | EA | THRESHOLD | 625A MSLA-10 | AL | ZER |

Perimeter weatherstripping by aluminum door manufacturer.  
  
Credential reader device and interfacing with the electric strike is by the security system supplier.

Hardware Group No. 03

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 1 | EA | PANIC HARDWARE | LD-99-EO | 626 | VON |
| 1 | EA | OH STOP | 100S | 630 | GLY |
| 1 | EA | SURFACE CLOSER | 4111 EDA | 689 | LCN |
| 1 | EA | MOUNTING PLATE | 4110-18 | 689 | LCN |
| 1 | EA | BLADE STOP SPACER | 4110-61 | 689 | LCN |
| 1 | EA | RAIN DRIP | 142A | AL | ZER |
| 1 | EA | DOOR SWEEP | 39A | AL | ZER |
| 1 | EA | THRESHOLD | 625A MSLA-10 | AL | ZER |

Perimeter weatherstripping by aluminum door manufacturer.

Hardware Group No. 04

Provide each PR door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 2 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 2 | EA | DUMMY PUSH BAR | 330 | 626 | VON |
| 2 | EA | 90 DEG OFFSET PULL | 8190HD 10" O | 630 | IVE |
| 2 | EA | OH STOP | 100S | 630 | GLY |
| 2 | EA | SURFACE CLOSER | 4111 EDA | 689 | LCN |
| 2 | EA | MOUNTING PLATE | 4110-18 | 689 | LCN |
| 2 | EA | BLADE STOP SPACER | 4110-61 | 689 | LCN |

Hardware Group No. 05

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 1 | EA | DUMMY PUSH BAR | 330 | 626 | VON |
| 1 | EA | 90 DEG OFFSET PULL | 8190HD 10" O | 630 | IVE |
| 1 | EA | OH STOP | 100S | 630 | GLY |
| 1 | EA | SURFACE CLOSER | 4111 EDA | 689 | LCN |
| 1 | EA | MOUNTING PLATE | 4110-18 | 689 | LCN |
| 1 | EA | BLADE STOP SPACER | 4110-61 | 689 | LCN |

Hardware Group No. 06

Provide each PR door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 2 | EA | CONT. HINGE | 224HD | 628 | IVE |
| 1 | EA | PANIC HARDWARE | LD-9949-EO | 626 | VON |
| 1 | EA | PANIC HARDWARE | LD-9949-L-NL-07 | 626 | VON |
| 1 | EA | RIM CYLINDER | 20-057 | 626 | SCH |
| 2 | EA | SURFACE CLOSER | 4111 SCUSH | 689 | LCN |
| 2 | EA | KICK PLATE | 8400 10" X 1" LDW B4E | 630 | IVE |
| 1 | EA | RAIN DRIP | 142A | AL | ZER |
| 1 | SET | SEALS | 328AA | AL | ZER |
| 2 | EA | MEETING STILE SEAL | 8193AA | AL | ZER |
| 2 | EA | DOOR SWEEP | 39A | AL | ZER |
| 1 | EA | THRESHOLD | 566A MSLA-10 | AL | ZER |

Mount head seal prior to mounting closer.

Hardware Group No. 07

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 224HD | 628 | IVE |
| 1 | EA | PANIC HARDWARE | LD-99-EO | 626 | VON |
| 1 | EA | SURFACE CLOSER | 4111 SCUSH | 689 | LCN |
| 1 | EA | KICK PLATE | 8400 10" X 2" LDW B4E | 630 | IVE |
| 1 | EA | RAIN DRIP | 142A | AL | ZER |
| 1 | SET | SEALS | 328AA | AL | ZER |
| 1 | EA | DOOR SWEEP | 39A | AL | ZER |
| 1 | EA | THRESHOLD | 566A MSLA-10 | AL | ZER |

Mount head seal prior to mounting closer.

Hardware Group No. 08

Provide each PR door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 2 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 2 | SET | PUSH/PULL BAR | 9103EZHD-10"-NO | 630 | IVE |
| 2 | EA | OH STOP | 100S | 630 | GLY |
| 2 | EA | SURFACE CLOSER | 4011 ST-1544 | 689 | LCN |
| 2 | EA | MOUNTING PLATE | 4020-18 | 689 | LCN |

Hardware Group No. 09

Provide each PR door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 2 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 2 | EA | MANUAL FLUSH BOLT | FB458 24" | 626 | IVE |
| 1 | EA | DUST PROOF STRIKE | DP2 | 626 | IVE |
| 1 | EA | DEADLOCK | MS1850S | 628 | ADA |
| 1 | EA | ADA THUMBTURN CYL | ADA7181TK1 | 626 | KAB |
| 1 | EA | MORTISE CYLINDER | 20-013 118 | 626 | SCH |
| 2 | SET | PUSH/PULL BAR | 9190HD-10"-NO | 630 | IVE |
| 2 | EA | OH STOP | 100S | 630 | GLY |
| 2 | EA | SURFACE CLOSER | 4011 ST-1544 | 689 | LCN |
| 2 | EA | MOUNTING PLATE | 4020-18 | 689 | LCN |

Key to be on the push side and thumbturn to be on the pull side.

Hardware Group No. 10

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 1 | EA | STOREROOM LOCK | ND80PD ATH | 626 | SCH |
| 1 | EA | SURFACE CLOSER | 4111 SCUSH | 689 | LCN |
| 1 | EA | MOUNTING PLATE | 4110-18 | 689 | LCN |
| 1 | EA | CUSH SHOE SUPPORT | 4110-30 | 689 | LCN |
| 1 | EA | BLADE STOP SPACER | 4110-61 | 689 | LCN |

Hardware Group No. 11

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 1 | EA | ENTRANCE/OFFICE LOCK | ND50PD ATH | 626 | SCH |
| 1 | EA | OH STOP & HOLDER | 100F ADJ | 630 | GLY |

Hardware Group No. 12

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | CONT. HINGE | 112HD | 628 | IVE |
| 1 | EA | CLASSROOM LOCK | ND70PD ATH | 626 | SCH |
| 1 | EA | OH STOP & HOLDER | 100F ADJ | 630 | GLY |

Hardware Group No. 13

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 | 652 | IVE |
| 1 | EA | STOREROOM LOCK | ND80PD ATH | 626 | SCH |
| 1 | EA | WALL STOP | WS406/407CCV | 630 | IVE |
| 1 | SET | SEALS | 188S | BLK | ZER |

Hardware Group No. 14

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 NRP | 652 | IVE |
| 1 | EA | STOREROOM LOCK | ND80PD ATH | 626 | SCH |
| 1 | EA | OH STOP & HOLDER | 90F | 630 | GLY |
| 1 | SET | SEALS | 188S | BLK | ZER |

Hardware Group No. 15

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 | 652 | IVE |
| 1 | EA | ENTRANCE/OFFICE LOCK | ND50PD ATH | 626 | SCH |
| 1 | EA | OH STOP & HOLDER | 90F J | 630 | GLY |

Hardware Group No. 16

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 | 652 | IVE |
| 1 | EA | ENTRANCE/OFFICE LOCK | ND50PD ATH | 626 | SCH |
| 1 | EA | WALL STOP | WS406/407CCV | 630 | IVE |

Hardware Group No. 17

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 | 652 | IVE |
| 1 | EA | CLASSROOM LOCK | ND70PD ATH | 626 | SCH |
| 1 | EA | WALL STOP | WS406/407CCV | 630 | IVE |

Hardware Group No. 18

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 | 652 | IVE |
| 1 | EA | PRIVACY LOCK | ND40S ATH | 626 | SCH |
| 1 | EA | WALL STOP | WS406/407CCV | 630 | IVE |

Hardware Group No. 19

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 3 | EA | HINGE | 5BB1 4.5 X 4.5 | 652 | IVE |
| 1 | EA | PASSAGE SET | ND10S ATH | 626 | SCH |
| 1 | EA | WALL STOP | WS406/407CCV | 630 | IVE |

Hardware Group No. 20

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | |  |  |  |  |  |
| Qty | | Description | Catalog Number | Finish | Mfr |
| 1 | EA | MORTISE CYLINDER | 20-062 | 626 | SCH |

All other hardware by door manufacturer.

Hardware Group No. 21

Provide each SGL door(s) with the following:

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |

All hardware by door manufacturer.

**End of Section**